## Products
PRODUCT NAME | EWYQ-CWN
[5 empty] | EWYQ016CAWN | EWYQ021CAWN | EWYQ025CAWN | EWYQ032CAWN | EWYQ040CAWN | EWYQ050CAWN | EWYQ064CAWN
Cooling capacity | Max. |  |  | kW | 20.0 | 25.0 | 30.1 | 37.6 | 50.1 | 60.1 | 75.2
| Nom. |  |  | kW | 16.8 (1) | 21.0 (1) | 25.3 (1) | 31.6 (1) | 42.1 (1) | 50.5 (1) | 63.2 (1)
Heating capacity | Max. |  |  | kW | 20.0 | 25.0 | 29.9 | 37.4 | 49.9 | 59.9 | 74.9
| Nom. |  |  | kW | 16.8 (2) | 21.0 (2) | 25.1 (2) | 31.4 (2) | 41.9 (2) | 50.3 (2) | 62.9 (2)
Capacity control | Method |  |  |  | Inverter controlled | Inverter controlled | Inverter controlled | Inverter controlled | Inverter controlled | Inverter controlled | Inverter controlled
| Minimum capacity |  |  | % | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Maximum capacity |  |  | % | 120 | 120 | 120 | 120 | 120 | 120 | 120
Power input | Cooling |  | Nom. | kW | 5.93 (1) | 7.61 (1) | 9.60 (1) | 12.9 (1) | 15.1 (1) | 19.2 (1) | 25.7 (1)
| Heating |  | Nom. | kW | 5.60 (2) | 6.89 (2) | 8.74 (2) | 10.8 (2) | 13.7 (2) | 17.5 (2) | 21.6 (2)
EER |  |  |  |  | 2.84 | 2.77 | 2.63 | 2.45 | 2.79 | 2.63 | 2.46
COP |  |  |  |  | 3.00 | 3.05 | 2.87 | 2.91 | 3.06 | 2.87 | 2.91
ESEER |  |  |  |  | 4.37 | 4.26 | 4.17 | 3.87 | 4.28 | 4.18 | 3.87
Dimensions | Packed unit |  | Depth | mm | 834 | 834 | 834 | 834 | 838 | 838 | 838
|  |  | Height | mm | 1,860 | 1,860 | 1,860 | 1,860 | 1,860 | 1,860 | 1,860
|  |  | Width | mm | 1,394 | 1,394 | 1,394 | 1,707 | 2,377 | 2,377 | 2,997
| Unit |  | Depth | mm | 774 | 774 | 774 | 774 | 780 | 780 | 780
|  |  | Height | mm | 1,684 | 1,684 | 1,684 | 1,684 | 1,684 | 1,684 | 1,684
|  |  | Width | mm | 1,370 | 1,370 | 1,370 | 1,680 | 2,360 | 2,360 | 2,980
Weight | Packed unit |  |  | kg | 295 | 348 | 348 | 434 | 624 | 624 | 794
| Unit |  |  | kg | 268 | 321 | 321 | 403 | 579 | 579 | 741
Packing | Material |  |  |  | Carton, Wood, Plastic | Carton, Wood, Plastic | Carton, Wood, Plastic | Carton, Wood, Plastic | Carton, Wood, Plastic | Carton, Wood, Plastic | Carton, Wood, Plastic
| Weight |  |  | kg | 27 | 27 | 27 | 31 | 45 | 45 | 53
Casing | Colour |  |  |  | Daikin White | Daikin White | Daikin White | Daikin White | Daikin White | Daikin White | Daikin White
| Material |  |  |  | Polyester coated galvanised steel plate | Polyester coated galvanised steel plate | Polyester coated galvanised steel plate | Polyester coated galvanised steel plate | Polyester coated galvanised steel plate | Polyester coated galvanised steel plate | Polyester coated galvanised steel plate
Water heat exchanger | Quantity |  |  |  | 1 | 1 | 1 | 1 | 2 | 2 | 2
| Type |  |  |  | Brazed plate | Brazed plate | Brazed plate | Brazed plate | Brazed plate | Brazed plate | Brazed plate
| Filter |  | Diameter perforations | mm | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0
|  |  | Material |  | Brass | Brass | Brass | Brass | Brass | Brass | Brass
| Water flow rate |  | Min. | l/min | 23 | 23 | 23 | 36 | 46 | 46 | 72
|  | Cooling | Nom. | l/min | 48 (3) | 60 (3) | 72 (3) | 90 (3) | 120 (3) | 145 (3) | 181 (3)
|  |  | Max | l/min | 72 | 90 | 108 | 136 | 181 | 217 | 271
|  | Heating | Nom. | l/min | 48 (2) | 60 (2) | 72 (2) | 90 (2) | 120 (2) | 145 (2) | 181 (2)
|  |  | Max | l/min | 72 | 90 | 108 | 136 | 181 | 217 | 271
| Water pressure drop | Cooling | Total | kPa | 8 | 10 | 14 | 8 | 10 | 14 | 8
| Water volume |  |  | l | 3 | 3 | 3 | 5 | 6 | 6 | 9
| Insulation material |  |  |  | Nitrile rubber based elastomeric foam | Nitrile rubber based elastomeric foam | Nitrile rubber based elastomeric foam | Nitrile rubber based elastomeric foam | Nitrile rubber based elastomeric foam | Nitrile rubber based elastomeric foam | Nitrile rubber based elastomeric foam
Air heat exchanger | Type |  |  |  | Air cooled coil | Air cooled coil | Air cooled coil | Air cooled coil | Air cooled coil | Air cooled coil | Air cooled coil
| Fin |  | Treatment |  | Hydrophylic and anti-corrosion resistant | Hydrophylic and anti-corrosion resistant | Hydrophylic and anti-corrosion resistant | Hydrophylic and anti-corrosion resistant | Hydrophylic and anti-corrosion resistant | Hydrophylic and anti-corrosion resistant | Hydrophylic and anti-corrosion resistant
|  |  | Type |  | Non-symmetric waffle louvre | Non-symmetric waffle louvre | Non-symmetric waffle louvre | Non-symmetric waffle louvre | Non-symmetric waffle louvre | Non-symmetric waffle louvre | Non-symmetric waffle louvre
| Fin pitch |  |  | mm | 2 | 2 | 2 | 2 | 2 | 2 | 2
Fan | Quantity |  |  |  | 1 | 1 | 1 | 2 | 2 | 2 | 4
| Type |  |  |  | Axial | Axial | Axial | Axial | Axial | Axial | Axial
| Air flow rate | Cooling | Nom. | m³/min | 171 | 185 | 185 | 233 | 370 | 370 | 466
|  | Heating | Nom. | m³/min | 171 | 185 | 185 | 233 | 370 | 370 | 466
| Discharge direction |  |  |  | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical
| External static pressure |  | Max. | Pa | 78 | 78 | 78 | 78 | 78 | 78 | 78
Fan motor | Drive |  |  |  | Direct drive | Direct drive | Direct drive | Direct drive | Direct drive | Direct drive | Direct drive
| Model |  |  |  | Brushless DC motor | Brushless DC motor | Brushless DC motor | Brushless DC motor | Brushless DC motor | Brushless DC motor | Brushless DC motor
| Quantity |  |  |  | 1 | 1 | 1 | 2 | 2 | 2 | 4
Refrigerant oil | Type |  |  |  | Synthetic (ether) oil | Synthetic (ether) oil | Synthetic (ether) oil | Synthetic (ether) oil | Synthetic (ether) oil | Synthetic (ether) oil | Synthetic (ether) oil
Compressor | Quantity |  |  |  | 1 | 2 | 2 | 3 | 4 | 4 | 6
| Type |  |  |  | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor
| Motor (INV) |  | Crankcase heater | W | 33 | 33 | 33 | 33 | 33 | 33 | 33
|  |  | Model |  | Inverter | Inverter | Inverter | Inverter | Inverter | Inverter | Inverter
|  |  | Quantity |  | 1 | 1 | 1 | 1 | 2 | 2 | 2
| Motor (ON-OFF) |  | Crankcase heater | W | 33 | 33 | 33 | 33 | 33 | 33 | 33
|  |  | Model |  | ON/OFF | ON/OFF | ON/OFF | ON/OFF | ON/OFF | ON/OFF | ON/OFF
|  |  | Quantity |  | 0 | 1 | 1 | 2 | 2 | 2 | 4
Operation range | Air side | Cooling | Max. | °CDB | 43 | 43 | 43 | 43 | 43 | 43 | 43
|  |  | Min. | °CDB | -5 | -5 | -5 | -5 | -5 | -5 | -5
|  | Heating | Max. | °CDB | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  |  | Min. | °CDB | -15 | -15 | -15 | -15 | -15 | -15 | -15
| Water side | Cooling | Max. | °CDB | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  | Min. | °CDB | -10 (4) | -10 (4) | -10 (4) | -10 (4) | -10 (4) | -10 (4) | -10 (4)
|  | Heating | Max. | °CDB | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  |  | Min. | °CDB | 25 | 25 | 25 | 25 | 25 | 25 | 25
Sound power level | Cooling |  | Nom. | dBA | 78 | 78 | 78 | 80 | 81 | 81 | 83
Refrigerant | Type |  |  |  | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
| GWP |  |  |  | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5
| Circuits |  | Quantity |  | 1 | 1 | 1 | 1 | 2 | 2 | 2
| Control |  |  |  | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve
Charge | Per circuit |  |  | kg | 7.60 | 7.60 | 7.60 | 9.60 | 7.60 | 7.60 | 9.60
| Per circuit |  |  | TCO2Eq | 15.9 | 15.9 | 15.9 | 20.0 | 15.9 | 15.9 | 20.0
Water circuit | Air purge valve |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Drain valve / fill valve |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| flowswitch |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Minimum water volume in the system for cooling |  |  | l | 33 (5) | 33 (5) | 33 (5) | 33 (5) | 66 (5) | 66 (5) | 66 (5)
| Minimum water volume in the system for heating |  |  | l | 76 (6) | 76 (6) | 76 (6) | 110 (6) | 152 (6) | 152 (6) | 220 (6)
| Nominal water pressure drop |  | Cooling | kPa | 12 (7) | 17 (7) | 23 (7) | 24 (7) | 19 (7) | 28 (7) | 29 (7)
| Piping |  |  | inch | 1-1/4" | 1-1/4" | 1-1/4" | 1-1/4" | 1-1/2" | 1-1/2" | 1-1/2"
| Piping connections diameter |  |  | inch | 1-1/4" (female) | 1-1/4" (female) | 1-1/4" (female) | 1-1/4" (female) | 2" (female) | 2" (female) | 2" (female)
| Safety valve |  |  | bar | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Shut off valve |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Total water volume |  |  | l | 4.2 (8) | 4.2 (8) | 4.2 (8) | 5.8 (8) | 7.9 (8) | 7.9 (8) | 11.0 (8)
PED | Category |  |  |  | Category II | Category II | Category II | Category II | Category II | Category II | Category II
| Most critical part |  | Name |  | Accumulator | Accumulator | Accumulator | Accumulator | Accumulator | Accumulator | Accumulator
|  |  | Ps*V | Bar*l | 335 | 335 | 335 | 385 | 335 | 335 | 385
Defrost method |  |  |  |  | Reversed cycle | Reversed cycle | Reversed cycle | Reversed cycle | Reversed cycle | Reversed cycle | Reversed cycle
Safety devices | Item |  | 01 |  | High pressure switch | High pressure switch | High pressure switch | High pressure switch | High pressure switch | High pressure switch | High pressure switch
|  |  | 02 |  | Overcurrent relay | Overcurrent relay | Overcurrent relay | Overcurrent relay | Overcurrent relay | Overcurrent relay | Overcurrent relay
|  |  | 03 |  | Inverter overload protector | Inverter overload protector | Inverter overload protector | Inverter overload protector | Inverter overload protector | Inverter overload protector | Inverter overload protector
|  |  | 04 |  | Fuse | Fuse | Fuse | Fuse | Fuse | Fuse | Fuse
General | Supplier/Manufacturer details |  | Name and address |  | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium
|  |  | Name or trademark |  | Daikin Europe N.V. | Daikin Europe N.V. | Daikin Europe N.V. | Daikin Europe N.V. | Daikin Europe N.V. | Daikin Europe N.V. | Daikin Europe N.V.
| Product description |  | Air-to-water heat pump |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  |  | Brine-to-water heat pump |  | No | No | No | No | No | No | No
|  |  | Heat pump combination heater |  | No | No | No | No | No | No | No
|  |  | Low-temperature heat pump |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  |  | Supplementary heater integrated |  | No | No | No | No | No | No | No
|  |  | Water-to-water heat pump |  | No | No | No | No | No | No | No
LW(A) Sound power level (according to EN14825) | dB(A) |  |  |  | 78 | 78 | 78 | 80 | 81 | 81 | 83
Sound condition Ecodesign and energy label |  |  |  |  | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825
Space heating general | Air to water unit |  | Rated airflow (outdoor) | m³/h | 10,260 | 11,100 | 11,100 | 13,980 | 22,200 | 22,200 | 27,960
| Other |  | Capacity control |  | Inverter | Inverter | Inverter | Inverter | Inverter | Inverter | Inverter
|  |  | Pck (Crankcase heater mode) | kW | 0.041 | 0.074 | 0.074 | 0.104 | 0.148 | 0.148 | 0.208
|  |  | Poff (Off mode) | kW | 0.041 | 0.074 | 0.074 | 0.104 | 0.148 | 0.148 | 0.208
|  |  | Psb (Standby mode) | kW | 0.041 | 0.074 | 0.074 | 0.104 | 0.148 | 0.148 | 0.208
|  |  | Pto (Thermostat off) | kW | 0.057 | 0.090 | 0.090 | 0.123 | 0.180 | 0.180 | 0.246
| Integrated supplementary heater |  | NOx emission | mg/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Psup | kW | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
|  |  | Type of energy input |  | Electrical | Electrical | Electrical | Electrical | Electrical | Electrical | Electrical
Space heating | Average climate water outlet 35°C | General | Annual energy consumption | kWh | 9,227 | 11,474 | 14,763 | 18,914 | 22,856 | 29,398 | 37,761
|  |  | Ƞs (Seasonal space heating efficiency) | % | 147 | 148 | 138 | 135 | 149 | 139 | 135
|  |  | Prated at -10°C | kW | 16.8 | 21.0 | 25.2 | 31.5 | 42.0 | 50.4 | 63.0
|  |  | Qhe Annual energy consumption (GCV) | Gj | 33 | 41 | 53 | 68 | 82 | 106 | 136
|  |  | SCOP |  | 3.75 | 3.78 | 3.53 | 3.45 | 3.80 | 3.55 | 3.45
|  |  | Seasonal space heating eff. class |  | A+ | A++ | A+ | A+ | A+ | A+ | A+
|  | A Condition (-7°CDB/-8°CWB) | Cdh (Degradation heating) |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0
|  |  | COPd |  | 2.42 | 2.43 | 2.32 | 2.12 | 2.43 | 2.32 | 2.12
|  |  | Pdh | kW | 14.8 | 18.4 | 20.5 | 26.7 | 36.8 | 41.1 | 53.4
|  |  | PERd | % | 96.8 | 97.2 | 92.8 | 84.8 | 97.2 | 92.8 | 84.8
|  | B Condition (2°CDB/1°CWB) | Cdh (Degradation heating) |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0
|  |  | COPd |  | 3.58 | 3.51 | 3.28 | 3.15 | 3.52 | 3.29 | 3.15
|  |  | Pdh | kW | 8.95 | 11.4 | 13.6 | 16.9 | 22.9 | 27.3 | 33.8
|  |  | PERd | % | 143.2 | 140.4 | 131.2 | 126.0 | 140.8 | 131.6 | 126.0
|  | C Condition (7°CDB/6°CWB) | Cdh (Degradation heating) |  | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0
|  |  | COPd |  | 4.98 | 5.27 | 5.02 | 5.35 | 5.31 | 5.05 | 5.38
|  |  | Pdh | kW | 5.81 | 7.34 | 8.55 | 10.8 | 14.7 | 17.1 | 21.6
|  |  | PERd | % | 199.2 | 210.8 | 200.8 | 214.0 | 212.4 | 202.0 | 215.2
|  | D Condition (12°CDB/11°CWB) | Cdh (Degradation heating) |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | COPd |  | 7.10 | 7.06 | 6.55 | 6.44 | 7.15 | 6.62 | 6.50
|  |  | Pdh | kW | 5.99 | 6.01 | 5.89 | 5.90 | 12.0 | 11.8 | 11.8
|  |  | PERd | % | 284.0 | 282.4 | 262.0 | 257.6 | 286.0 | 264.8 | 260.0
|  | Rated heat output supplementary capacity | Psup (at Tdesign -10°C) | kW | 2.10 | 2.10 | 6.00 | 8.00 | 4.10 | 11.9 | 15.9
|  | Tbiv (bivalent temperature) | COPd |  | 2.30 | 2.28 | 2.34 | 2.14 | 2.28 | 2.35 | 2.14
|  |  | Pdh | kW | 15.7 | 20.0 | 20.8 | 26.7 | 40.1 | 41.6 | 53.4
|  |  | PERd | % | 92.0 | 91.2 | 93.6 | 85.6 | 91.2 | 94.0 | 85.6
|  |  | Tbiv | °C | -8 | -8 | -6 | -6 | -8 | -6 | -6
|  | Tol (temperature operating limit) | COPd |  | 2.16 | 2.15 | 2.13 | 1.86 | 2.16 | 2.13 | 1.86
|  |  | Pdh | kW | 14.7 | 18.9 | 19.2 | 23.5 | 37.9 | 38.5 | 47.1
|  |  | PERd | % | 86.4 | 86.0 | 85.2 | 74.4 | 86.4 | 85.2 | 74.4
|  |  | TOL | °C | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | WTOL | °C | 35 | 35 | 35 | 35 | 35 | 35 | 35
| Cold climate water outlet 35°C | General | Annual energy consumption | kWh | 16,150 | 18,158 | 25,431 | 36,359 | 36,042 | 52,913 | 75,408
|  |  | Ƞs (Seasonal space heating efficiency) | % | 109 | 113 | 107 | 111 | 114 | 102 | 106
|  |  | Prated at -22°C | kW | 18.3 | 21.4 | 28.3 | 41.9 | 42.7 | 56.6 | 83.7
|  |  | Qhe Annual energy consumption (GCV) | Gj | 58 | 65 | 92 | 131 | 130 | 190 | 271
| Warm climate water outlet 35°C | General | Annual energy consumption | kWh | 5,601 | 6,981 | 8,060 | 10,830 | 13,961 | 16,061 | 21,354
|  |  | Ƞs (Seasonal space heating efficiency) | % | 161 | 158 | 154 | 154 | 158 | 155 | 156
|  |  | Prated at 2°C | kW | 17.2 | 21.0 | 23.7 | 31.8 | 42.1 | 47.5 | 63.7
|  |  | Qhe Annual energy consumption (GCV) | Gj | 20 | 25 | 29 | 39 | 50 | 58 | 77
Power supply | Name |  |  |  | W1 | W1 | W1 | W1 | W1 | W1 | W1
| Phase |  |  |  | 3N~ | 3N~ | 3N~ | 3N~ | 3N~ | 3N~ | 3N~
| Frequency |  |  | Hz | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10 | 10
Unit | Starting current |  | Max | A | 0.0 (9) | 77.7 | 78.7 | 88.7 | 99.8 | 101.9 | 120.7
| Current | Zmax | Text |  | 0,22 | 0,27 | 0,27 | 0,24 | 0,25 | 0,25 | 0,22
| Running current |  | Max | A | 22.2 | 25.3 | 26.4 | 35.2 | 47.4 | 49.6 | 67.2
| Minimum Ssc value |  |  |  | 1,141 | 853 | 853 | 840 | 1,706 | 1,706 | 1,679
| Recommended fuses |  |  | A | 25 | 32 | 32 | 40 | 50 | 63 | 80
Cable requirements | Power supply |  | Required number of conductors |  | 4 + GND | 4 + GND | 4 + GND | 4 + GND | 4 + GND | 4 + GND | 4 + GND
| Remote control |  | Quantity of wires |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Maximum running current |  | Minimum cable section 0,75 mm² | Minimum cable section 0,75 mm² | Minimum cable section 0,75 mm² | Minimum cable section 0,75 mm² | Minimum cable section 0,75 mm² | Minimum cable section 0,75 mm² | Minimum cable section 0,75 mm²
| Cooling/Heating output |  | Quantity of wires |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Maximum running current | A | 0,3 | 0,3 | 0,3 | 0,3 | 0,3 | 0,3 | 0,3
| Operation ON/OFF output |  | Quantity of wires |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Maximum running current | A | 0,3 | 0,3 | 0,3 | 0,3 | 0,3 | 0,3 | 0,3
| Error output |  | Quantity of wires |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Maximum running current | A | 0,3 | 0,3 | 0,3 | 0,3 | 0,3 | 0,3 | 0,3
| Pump ON/OFF output |  | Quantity of wires |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Maximum running current | A | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Notes |  |  |  |  | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C
[5 empty] | (2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | (2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | (2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | (2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | (2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | (2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | (2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)
[5 empty] | (3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | (3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | (3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | (3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | (3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | (3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | (3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)
[5 empty] | (4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option) | (4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option) | (4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option) | (4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option) | (4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option) | (4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option) | (4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option)
[5 empty] | (5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | (5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | (5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | (5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | (5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | (5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | (5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.
[5 empty] | (6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils) | (6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils) | (6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils) | (6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils) | (6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils) | (6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils) | (6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)
[5 empty] | (7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop. | (7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop. | (7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop. | (7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop. | (7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop. | (7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop. | (7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.
[5 empty] | (8) - Including piping + PHE; excluding expansion vessel | (8) - Including piping + PHE; excluding expansion vessel | (8) - Including piping + PHE; excluding expansion vessel | (8) - Including piping + PHE; excluding expansion vessel | (8) - Including piping + PHE; excluding expansion vessel | (8) - Including piping + PHE; excluding expansion vessel | (8) - Including piping + PHE; excluding expansion vessel
[5 empty] | (9) - No peak current because of inverter compressor | (9) - No peak current because of inverter compressor | (9) - No peak current because of inverter compressor | (9) - No peak current because of inverter compressor | (9) - No peak current because of inverter compressor | (9) - No peak current because of inverter compressor | (9) - No peak current because of inverter compressor