## Products
PRODUCT NAME | EWAQ-G-XS
[5 empty] | EWAQ080G-XS | EWAQ090G-XS | EWAQ105G-XS | EWAQ115G-XS | EWAQ130G-XS | EWAQ150G-XS
Cooling capacity | Nom. |  |  | kW | 79.79 | 90.26 | 105.3 | 116.8 | 130 | 149
| Rated |  |  | kW | 79.79 | 90.26 | 105.3 | 116.8 | 130 | 149
Capacity control | Method |  |  |  | Staged | Staged | Staged | Staged | Staged | Staged
| Minimum capacity |  |  | % | 50 | 44 | 50 | 44 | 50 | 43
Power input | Cooling |  | Nom. | kW | 25.75 | 29.04 | 33.75 | 37.68 | 42.26 | 48.09
EER |  |  |  |  | 3.099 | 3.108 | 3.121 | 3.099 | 3.1 | 3.099
ESEER |  |  |  |  | 4.2 | 4.3 | 4.28 | 4.34 | 4.22 | 4.36
IPLV |  |  |  |  | 4.82 | 5.04 | 4.96 | 5.02 | 4.92 | 5.05
SEER |  |  |  |  | 3.95 | 4.188 | 4.254 | 4.224 | 4.314 | 4.21
Dimensions | Unit |  | Depth | mm | 2,680 | 3,200 | 3,200 | 3,200 | 3,800 | 3,800
|  |  | Height | mm | 1,800 | 1,800 | 1,800 | 1,800 | 1,820 | 1,820
|  |  | Width | mm | 1,195 | 1,195 | 1,195 | 1,195 | 1,195 | 1,195
Weight | Operation weight |  |  | kg | 744 | 860 | 1,002 | 1,040 | 1,102 | 1,144
| Unit |  |  | kg | 734 | 850 | 987 | 1,024 | 1,086 | 1,123
Casing | Colour |  |  |  | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white
| Material |  |  |  | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet
Water heat exchanger | Type |  |  |  | Braze plate heat exchanger | Braze plate heat exchanger | Braze plate heat exchanger | Braze plate heat exchanger | Braze plate heat exchanger | Braze plate heat exchanger
| Water flow rate | Cooling | Nom. | l/s | 3.8 | 4.3 | 5 | 5.6 | 6.3 | 7.1
| Water pressure drop | Cooling | Nom. | kPa | 25.7 | 32.7 | 20.3 | 19.9 | 25.4 | 20.6
| Water volume |  |  | l | 5.58 | 4.86 | 4.86 | 5.6 | 5.6 | 8.1
| Insulation material |  |  |  | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell
Air heat exchanger | Type |  |  |  | Microchannel | Microchannel | Microchannel | Microchannel | Microchannel | Microchannel
Heat exchanger | Indoor side |  |  |  | water | water | water | water | water | water
| Outdoor side |  |  |  | Air | Air | Air | Air | Air | Air
Fan | Quantity |  |  |  | 6 | 6 | 8 | 8 | 10 | 10
| Type |  |  |  | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller
| Air flow rate |  | Nom. | l/s | 9,029 | 9,498 | 12,008 | 12,008 | 15,046 | 15,046
|  | Cooling | Rated | m³/h | 32,539.31 | 34,203.89 | 43,280.11 | 43,280.11 | 54,223.87 | 54,223.87
| Diameter |  |  | mm | 450 | 450 | 450 | 450 | 450 | 450
| Speed |  |  | rpm | 1,360 | 1,360 | 1,360 | 1,360 | 1,360 | 1,360
Fan motor | Drive |  |  |  | DOL | DOL | DOL | DOL | DOL | DOL
| Input |  | Cooling | W | 2,700 | 2,700 | 3,600 | 3,600 | 4,500 | 4,500
Compressor | Quantity |  |  |  | 2 | 2 | 2 | 2 | 2 | 2
| Type |  |  |  | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression
| Driver |  |  |  | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor
| Oil |  | Charged volume | l | 6.76 | 8.05 | 9.34 | 11.47 | 13.6 | 13.6
Operation range | Air side | Cooling | Max. | °CDB | 45 | 45 | 45 | 45 | 45 | 45
|  |  | Min. | °CDB | -10 | -10 | -10 | -10 | -10 | -10
| Water side | Cooling | Max. | °CDB | 15 | 15 | 15 | 15 | 15 | 15
|  |  | Min. | °CDB | -10 | -10 | -10 | -10 | -10 | -10
Sound power level | Cooling |  | Nom. | dBA | 84 | 85 | 87 | 89 | 89 | 89
Sound pressure level | Cooling |  | Nom. | dBA | 66 | 68 | 69 | 71 | 71 | 71
Refrigerant | Type |  |  |  | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
| GWP |  |  |  | 2,088 | 2,088 | 2,088 | 2,088 | 2,088 | 2,088
| Circuits |  | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
| Charge |  |  | kg | 9.1 | 12.7 | 13.1 | 13.2 | 16.1 | 15
Charge | Per circuit |  |  | TCO2Eq | 19 | 26.5 | 27.3 | 27.6 | 33.6 | 31.3
Piping connections | Evaporator water inlet/outlet (OD) |  |  |  | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2
Space cooling | A Condition 35°C |  | Pdc | kW | 79.8 | 90.3 | 105.3 | 116.8 | 130.0 | 149.0
|  |  | EERd |  | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
| B Condition 30°C |  | Pdc | kW | 59.1 | 61.4 | 76.4 | 77.8 | 96.9 | 102.9
|  |  | EERd |  | 4.0 | 4.4 | 4.2 | 4.2 | 4.1 | 4.1
| C Condition 25°C |  | Pdc | kW | 37.5 | 42.4 | 49.5 | 54.9 | 61.6 | 70.0
|  |  | EERd |  | 4.8 | 4.9 | 5.0 | 4.9 | 5.1 | 4.8
| D Condition 20°C |  | Pdc | kW | 16.8 | 19.0 | 22.1 | 24.5 | 27.5 | 31.3
|  |  | EERd |  | 4.9 | 5.2 | 5.3 | 5.1 | 5.3 | 5.0
| ηs,c |  |  | % | 155.0 | 164.5 | 167.2 | 166.0 | 169.6 | 165.4
General | Supplier/Manufacturer details |  | Name and address |  | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy
LW(A) Sound power level (according to EN14825) | dB(A) |  |  |  | 84 | 85 | 87 | 89 | 89 | 89
Cooling | Cdc (Degradation cooling) |  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Standard rating conditions used |  |  |  |  | Low temperature application | Medium temperature application | Medium temperature application | Medium temperature application | Medium temperature application | Medium temperature application
Power consumption in other than active mode | Crankcase heater mode |  | PCK | W | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066
| Off mode |  | POFF | W | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000
| Standby mode | Cooling | PSB | W | 0.100 | 0.100 | 0.100 | 0.100 | 0.100 | 0.100
| Thermostat-off mode | PTO | Cooling | W | 0.136 | 0.136 | 0.156 | 0.156 | 0.156 | 0.156
Power supply | Phase |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
| Frequency |  |  | Hz | 50 | 50 | 50 | 50 | 50 | 50
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10
Unit | Starting current |  | Max | A | 213 | 264 | 272 | 319 | 329 | 367
| Running current | Cooling | Nom. | A | 52 | 56 | 61 | 69 | 76 | 87
|  |  | Max | A | 70 | 75 | 83 | 91 | 101 | 116
| Max unit current for wires sizing |  |  | A | 77 | 83 | 91 | 100 | 111 | 128
Fans | Nominal running current (RLA) |  |  | A | 6 | 6 | 8 | 8 | 10 | 10
Compressor | Phase |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10
| Maximum running current |  |  | A | 62 | 67 | 73 | 81 | 89 | 104
| Starting method |  |  |  | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line
Notes |  |  |  |  | (1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.
[5 empty] | (2) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated form sound power level and used for info only, not considered bounding | Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated form sound power level and used for info only, not considered bounding | Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated form sound power level and used for info only, not considered bounding | Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated form sound power level and used for info only, not considered bounding | Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated form sound power level and used for info only, not considered bounding | Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated form sound power level and used for info only, not considered bounding
[5 empty] | (3) - Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water
[5 empty] | (4) - For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS).
[5 empty] | (5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.
[5 empty] | (6) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.
[5 empty] | (7) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.
[5 empty] | (8) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.
[5 empty] | (9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current
[5 empty] | (10) - Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage.
[5 empty] | (11) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1
[5 empty] | (12) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)
[5 empty] | (13) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory
[5 empty] | (14) - For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book